## Explanations
This file contains the data that has been used to plot the curves presented in Case Study No. 10:
- state of the different points (T, P, x, v)
- flows of the expansion processes, polytropic efficiency of these processes.
Refer to the Flamanville model diagram file Fla3_99_P1RT_Rechauff.dia to identify the names of the points and processes

## Data
fraction | 0.3 | 0.5 | 0.7 | 0.9 | 1
Temperature (°C)
P1RT | 206.00403961 | 236.37900676 | 259.31268803 | 277.91868447 | 286.27148598
F | 293.3 | 289 | 284.8 | 279.1824991 | 275.14667342
G | 293.2941372 | 288.99952033 | 284.79163146 | 279.1824991 | 275.13273157
K2 | 19.88516 | 23.01389 | 26.10206 | 29.11185 | 30.72013
HP1 | 168.2735018 | 192.72912452 | 210.55529811 | 224.91382835 | 231.26410759
H3_vap | 63.98896678 | 76.02322 | 84.49585 | 91.04895045 | 93.91698
HP3 | 136.06509093 | 155.14542497 | 168.77833253 | 179.5572774 | 184.26863155
FP | 136.76836371 | 157.7040993 | 168.68301307 | 177.44716252 | 181.90869632
IP2 | 165.37055951 | 161.29224719 | 157.55919978 | 153.22573438 | 151.35288062
HP2 | 154.60115048 | 176.86181388 | 193.00581106 | 205.92113749 | 211.63719323
EP | 20.026479 | 23.0967822 | 26.18951597 | 29.20361925 | 30.87744963
IP1 | 231.125924 | 226.80992987 | 222.59983058 | 217.50240809 | 215.26528797
LP1 | 63.98896678 | 76.0232175 | 84.49584986 | 91.04895045 | 93.91698139
LP3 | 33.76891511 | 42.28018207 | 48.48981623 | 53.40983113 | 55.57504456
C2 | 298.75886051 | 298.39344812 | 294.852013 | 289.89563704 | 287.44110935
LP2 | 49.47923054 | 60.10796421 | 67.61159051 | 73.42633461 | 75.96940862
LP4 | 19.88516313 | 23.01389211 | 26.10205553 | 29.11185436 | 30.64063838
sBA | 135.43936982 | 156.1917703 | 167.09917724 | 175.93335887 | 180.3712448
SG | 302.40825129 | 301.69751359 | 299.2305981 | 294.96755403 | 293.20565921
G1_vap | 49.47923054 | 60.10796421 | 67.61159051 | 73.42633461 | 75.96941
G_vap | 33.76891511 | 42.28018207 | 48.48981623 | 53.40983113 | 55.57504456
Pressure (bar)
P1RT | 17.6 | 31.398 | 46.4217 | 62.21 | 70.5
F | 3.11 | 5.244 | 7.4 | 9.543 | 10.62
G | 3.105 | 5.244 | 7.394 | 9.543 | 10.61
K2 | 0.0232 | 0.0281 | 0.0338 | 0.0403 | 0.0442
HP1 | 7.595 | 13.32 | 19.29 | 25.46 | 28.63
H3_vap | 0.239 | 0.4023 | 0.5667 | 0.7295 | 0.8121
HP3 | 3.229 | 5.454 | 7.689 | 9.925 | 11.05
FP | 93.73 | 93.08 | 91.5 | 88.2 | 86.5
IP2 | 0.9738 | 1.63 | 2.287 | 2.942 | 3.27
HP2 | 5.377 | 9.323 | 13.4 | 17.57 | 19.71
EP | 19 | 19 | 19 | 19 | 19
IP1 | 1.783 | 2.999 | 4.217 | 5.432 | 6.041
LP1 | 0.239 | 0.4023 | 0.5667 | 0.7295 | 0.8121
LP3 | 0.0525 | 0.0832 | 0.1144 | 0.1458 | 0.1618
C2 | 84.435 | 84 | 79.867 | 74.347 | 71.725
LP2 | 0.1202 | 0.2002 | 0.2808 | 0.3608 | 0.4014
LP4 | 0.0232 | 0.0281 | 0.0338 | 0.0403 | 0.044
sBA | 10 | 8 | 7.689 | 12 | 11.11
SG | 88.88 | 88 | 85 | 80 | 78
G1_vap | 0.1202 | 0.2002 | 0.2808 | 0.3608 | 0.4014
G_vap | 0.0525 | 0.0832 | 0.1144 | 0.1458 | 0.1618
Quality
P1RT | 0.971221549 | 0.965981693 | 0.969961837 | 0.982475448 | 0.990965824
HP1 | 0.920626415 | 0.906682043 | 0.899057034 | 0.896394016 | 0.895750098
H3_vap | 0.990161924 | 0.977066358 | 0.966126533 | 0.964350867 | 0.959733659
HP3 | 0.884853749 | 0.867690925 | 0.857024115 | 0.850690544 | 0.848095683
HP2 | 0.904490079 | 0.889095157 | 0.879853687 | 0.875219663 | 0.873524663
LP1 | 0.99016095 | 0.977064117 | 0.96612326 | 0.964347429 | 0.951409501
LP3 | 0.955342434 | 0.946036741 | 0.939414465 | 0.937584299 | 0.915456819
C2 | 0.990014415 | 0.991367854 | 0.990760349 | 0.991591982 | 0.991970058
LP2 | 0.971917853 | 0.96142259 | 0.953208447 | 0.951385656 | 0.931845629
LP4 | 0.927469416 | 0.913271969 | 0.904371828 | 0.901593654 | 0.898945271
SG | 0.994805779 | 0.995652498 | 0.995963529 | 0.996858146 | 0.997585489
G1_vap | 0.971920582 | 0.961426299 | 0.953212907 | 0.951390281 | 0.947341338
G_vap | 0.9553467 | 0.946041846 | 0.939420157 | 0.937590151 | 0.934957033
Volume (m3/kg)
P1RT | 0.109544994 | 0.0615215653 | 0.0413873044 | 0.0306613145 | 0.0269230774
F | 0.833948793 | 0.487910649 | 0.34095142 | 0.259818824 | 0.230775672
G | 0.835293569 | 0.487910211 | 0.341228397 | 0.259818824 | 0.230993907
K2 | 0.001001701 | 0.00100239718 | 0.00100318371 | 0.00100403985 | 0.00100453197
HP1 | 0.232451145 | 0.133963319 | 0.0928262112 | 0.0704677181 | 0.0626670314
H3_vap | 6.40833481 | 3.88095758 | 2.7841681 | 2.19405417 | 1.97503359
HP3 | 0.500225874 | 0.299673596 | 0.213960046 | 0.166642537 | 0.14995926
FP | 0.00107108987 | 0.00109328528 | 0.00110629403 | 0.00111755495 | 0.00112355952
IP2 | 2.06365638 | 1.21480258 | 0.853245438 | 0.65213609 | 0.582016926
HP2 | 0.316551527 | 0.184807869 | 0.129286903 | 0.0989962777 | 0.0883470089
EP | 0.00100086684 | 0.00100156034 | 0.00100235595 | 0.00100321977 | 0.00100373552
IP1 | 1.2959706 | 0.759756907 | 0.53257543 | 0.406438846 | 0.362484825
LP1 | 6.40832851 | 3.88094865 | 2.78415867 | 2.19404635 | 1.95791235
LP3 | 25.72391271 | 16.50665898 | 12.14684423 | 9.6514695 | 8.54543058
C2 | 0.0218908172 | 0.0220513086 | 0.0233655083 | 0.0253758677 | 0.0264335372
LP2 | 11.99597823 | 7.3477993 | 5.30359249 | 4.18484376 | 3.70916129
LP4 | 54.00542229 | 44.36692916 | 36.89953775 | 31.15702534 | 28.59396538
sBA | 0.00107496708 | 0.00109760856 | 0.00111080206 | 0.00112186 | 0.00112793738
SG | 0.0207017782 | 0.0209637154 | 0.0218429018 | 0.023455706 | 0.0241644946
G1_vap | 11.99601192 | 7.34782764 | 5.3036173 | 4.1848641 | 3.77082406
G_vap | 25.72402758 | 16.50674805 | 12.14691781 | 9.65152974 | 8.72743582
Flow rate (kg/s)
HP1 turbine | 563.725 | 1006.844 | 1496.73 | 2016.704 | 2288.362
HP2 turbine | 546.24542755 | 961.58 | 1399.616 | 1855.582 | 2090.80119908
HP3 turbine | 526.54342755 | 919.335 | 1329.475 | 1752.817 | 1971.22919908
IP1 turbine | 455.38682675 | 774.81838456 | 1099.51477786 | 1434.51365052 | 1603.7902607
IP2 turbine | 440.53982675 | 746.56238456 | 1056.29477786 | 1375.10365052 | 1535.5722607
LP1 turbine | 416.00282675 | 696.41238456 | 981.79477786 | 1277.74665052 | 1423.9812607
LP2 turbine | 394.98041744 | 655.96978728 | 919.88145186 | 1193.03209502 | 1316.11249584
LP3 turbine | 389.90830825 | 644.34725672 | 901.31214759 | 1168.82129518 | 1288.0637792
LP4 turbine | 376.55956702 | 614.36177961 | 852.89268694 | 1103.0759999 | 1212.41388702
Efficiency
Extraction pump | 0.8 | 0.9 | 0.9 | 0.9 | 0.8
Feedwater pump | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HP1 turbine | 0.897263334 | 0.894273636 | 0.895508429 | 0.900877151 | 0.903102183
HP2 turbine | 0.887239581 | 0.882416644 | 0.882133906 | 0.883405953 | 0.884670995
HP3 turbine | 0.857290172 | 0.863051487 | 0.862536488 | 0.863847496 | 0.864431771
IP1 turbine | 0.896045341 | 0.896038649 | 0.898356558 | 0.896430447 | 0.873340154
IP2 turbine | 0.9741664 | 0.973782028 | 0.974108275 | 0.973181289 | 0.972581214
LP1 turbine | 0.873169186 | 0.869999999 | 0.868922986 | 0.782655025 | 0.861349348
LP2 turbine | 0.685311338 | 0.629108857 | 0.57890081 | 0.57889282 | 0.888645716
LP3 turbine | 0.615130379 | 0.583435045 | 0.557470714 | 0.556833137 | 0.871951167
LP4 turbine | 0.901451036 | 0.839487147 | 0.819430336 | 0.805557323 | 0.801529046